Water Improvement

General Notes

1. All work shall be done in accordance with this plan and the current standard drawings and specifications of the City of Chino Hills Engineering Department and the Standard Specifications for Public Works Construction, 2003 edition.

2. The hours of operation shall be from 6:00 AM to 7:00 PM, Monday through Friday. Other hours shall require written authorization from the City Engineer or City Building Official.

3. No work shall be undertaken without obtaining all necessary permits from the City. The site superintendent or foreman shall notify the Engineering Inspector  (909) 364-2770 at least 48 hours in advance of any inspections required.

4. State Law SB 3019 requires the contractor to obtain an identification number from Underground Service Alert prior to the issuance of a city encroachment permit. The contractor shall notify Underground Service Alert two full working days (48 hours minimum) in advance of any construction activities, including pavement removal, excavation and AC overlay, which could affect any underground utility.

5. Any contractor performing work on this project shall familiarize himself with the site and shall be responsible for any damage to existing facilities resulting directly or indirectly from his operations, whether or not such facilities are shown on the plans.

6. Prior to any construction work which could damage or conflict with underground structures or utilities, the contractor shall excavate inspection holes to determine the location and depth of said structures and utilities in the vicinity of, or which may be affected by, the proposed improvement work.

7. Prior to construction the contractor shall expose and verify the location and elevation of any existing pipeline which is to be joined.

8. Domestic and recycled water mains between 4-inches and 12-inches in diameter shall be either AWWA C-900 PVC (Class 200 minimum), cement mortar lined and coated steel pipe (CML&CSP) 10 Ga. Min. For pipe sizes 14-inches or larger, CML&CSP or AWWA C-905 PVC (Class 235 minimum) must be used. All pipes shall meet the specifications as indicated in the City of Chino Hills Standard Drawings and Specifications for Water, Reclaimed Water and Wastewater Facilities.

9. Unless otherwise approved domestic water mains shall be located seven (7’) feet from curb face on the south or west side of the street and recycled water mains shall be located seven (7’) feet from curb face on the north or east side of the street.

10. All domestic and recycled water mains shall be constructed with a minimum cover of 48-inches for pipes 12-inches in diameter and larger or 42” cover for 10-inches in diameter and smaller. Cover shall be measured from the outside diameter of the pipe to finish surface above.

11. A minimum horizontal separation of ten (10’) feet shall be maintained between sewer and domestic water mains and five (5’) feet between sewer and recycled water mains. A minimum of five (5’) feet shall be kept between sewer lateral and water services.

12. A 14 ga. copper wire shall be laid on top of non-metallic mains and wrapped around the main at 10’ intervals with conducting connections to the valves.

13. Pressure testing and chlorination shall be performed in accordance with the City of Chino Hills Standards and Specifications. Pressure tests shall not be made on closed valves. The maximum length for a test shall be 4,000 feet.

14. Connections to existing water mains shall be done by the contractor at a pre-arranged time and under the supervision of the Public Works Inspector and Public Facilities and Operations Supervisor. Shutoffs shall be scheduled to include a 24-hour notice before proceeding.

15. The contractor shall operate no existing mainline water valves.

16. No pipeline shall be installed on fill material without first meeting in place density tests required by the city. Compaction in intermediate zone shall be compacted to 90% relative density.  

17. No water shall be obtained from any City fire hydrant without the use of an authorized hydrant meter.

18. Survey monuments shall be protected and perpetuated in place. Any disturbed or covered monuments shall be reset by a Registered Civil Engineer or Licensed Land Surveyor.

19. If existing utilities or other facilities conflict with the proposed improvements, work shall stop and the engineer be notified immediately.

20. The contractor shall repair or replace any public improvements damaged as a result of construction as required by the Public Works Inspector.

21. The contractor shall maintain dust control at all times.

22. Trench backfill shall be done in accordance with City Standard Drawing No. W-3.

23. “As-built” record drawings shall be furnished to the city upon completion of the project. Record drawing shall indicate constructed location of all water laterals, stubs for future connection and manhole locations.

24. Approval of these plans by the City or its agents shall not relieve the contractor or the applicant of the responsibility for correction of errors or omissions discovered during construction. Upon request, the appropriate plan revisions shall be promptly submitted to the City Engineer for review and approval.

25. Estimate of quantities is provided by the engineer only for the convenience of the developer. The contractor shall make his own determination of construction quantities before submitting a bid. Any item of work required by these plans, which is not specifically listed in the estimate of quantities, shall be considered as included in the other items of work.

